## Slide 1: 5.0 Three Phase Theory and Symmetrical Components
EE1203 – Theory of Electricity
Prof J. Rohan Lucas
lucas@kdu.ac.lk
Department of Electrical, Electronic & Telecommunication Engineering
General Sir John Kotelawala Defence University
September 2020
Lecture 9
Notes: Dear students. In the next set of lessons, we will be studying the application of balanced and unbalanced three phase theory to circuits. Will then learn how unbalanced voltages and currents may be broken up into 3 sequence components.

## Slide 2: Learning Outcomes
t
On completion of module, student will be able to
LO1: Analyse the performances of AC circuits
Analyse circuits using nodal and mesh theory
LO2: Analyse two port networks using different models.
LO3: Analyse transfer functions of RLC networks for transients.
LO4: Analyse waveforms for its harmonics.
LO5: Perform calculations in three phase circuits including unbalanced waveforms.
Notes: .The learning outcomes of this set of lessons is to be able to perform calculations in three phase circuits including unbalanced waveforms and sequence components.

## Slide 3: Three Phase Theory and Symmetrical Components
Figure 1(a) – Three phase waveforms
Single phase a.c. – 2 wires (live and neutral) required.
Distribution lines usually have 4 wires (3 phase wires, and neutral).
Phases are usually designated A, B, C (earlier red, yellow, blue)
A
B
C

## Slide 4: Balanced three phase
Three phases are usually 120o out of phase
Phasor addition zero if supply is balanced.
Figure 1(b)
Phasor Diagram
N
VA
VB
VC
phase voltage Vp – voltage between any one phase and neutral, phase-to-neutral voltage.
line voltage VL – voltage between any two lines, line-to-line voltage.
If A-phase voltage VA = Vp0,
then VB = Vp-2p/3 and VC = Vp-4p/3.

## Slide 5: Balanced Three Phase Supply
VAB
VBC
VCA
Figure 2(b) Delta-connected supply
Id
IL
VL
VA
VB
VC
Figure 2(a) Star-connected supply
IL
IP
VP
VL
Can be connected either in star or in delta.

## Slide 6
In a balanced three phase system, knowledge of one of the phases gives the other two phases directly.
VRY = VR – VY, VYB = VY – VB, and VBR = VB – VR.
VR
VY
VB
-VR
-VB
-VY
VR
VY
VB
VBR
VYB
VBR
VRY
VYB
VRY
Figure 3(b) Triangular addition
Figure 3(a) Parallelogram addition

## Slide 7
For a balanced star system, the angles between the phases is 120o and the magnitudes are all equal.
Line voltages would lead by 300 the nearest phase voltage.
IL = IP , VL = 3VP
Similarly with a delta connected supply, the current
IL = 3Id, VL = Vd
Line voltages must be specified in a sequential manner.
i.e. VRY, VYB and VBR.
[Note: VBY is 1800 out of phase with VYB so that the corresponding angles if this is chosen may appear to be 600 rather than 1200].

## Slide 8
VR
VY
VB
-VR
-VB
-VY
VYB
VBR
VRY
If the direction of VR is selected as reference, then
VR = Vp0 = Vp0o,
VY = Vp-2p/3 = Vp-120o,
VB = Vp-4p/3 = Vp-240o
VRY = 3Vpp/6 = 3Vp30o,
VYB = 3Vp-p/2 = 3Vp-90o,
VBR = 3Vp-7p/6 = 3Vp-210o

## Slide 9: Balanced Load
VR
VY
VB
IB
IR
IY
Figure 4(a) Phasor Diagram
A balanced load would have impedances of the three phases equal in magnitude and in phase.
With balanced supply (Figure 4(a))
phase voltages differ by 1200
phase currents differ by 1200
loads have same phase angle
Two configurations:
star connection
delta connection.

## Slide 10: For same balanced load
each phase will have same impedance
star impedance and delta impedance will be different.
ZD = 3 Zs
phase angle of impedance, of star and of delta, is the same.
Note: In the delta, the voltage is 3 times larger and the current 3 times smaller, giving the impedance 3 times larger.
The equivalent power is unaffected by transformation.
Zs
Zs
Zs
ZD
ZD
ZD
(b) Star connection
(c) Delta connection
Figure 4

## Slide 11: Three Phase Power
With single phase, P = V I cos f
With three phase, P = 3 Vp Ip cos f
Neutral not always available to measure phase voltage.
Also current inside delta not be directly available.
Usual to express power associated in terms of line voltage VL and line current IL.
For balanced star connected load,
Vstar = VL /Ö3, Istar = IL
Zstar = Vstar / Istar = VL /Ö3IL
Sstar = 3VstarIstar* = Ö3VLIL*

## Slide 12
Thus Pstar = Ö3VLIL cos f,
Qstar = Ö3VLIL sin f
For a balanced delta connected load,
Vdelta = VL, Idelta = IL /Ö3
Zdelta = Vdelta / Idelta = Ö3VL / IL
Sdelta = 3VdeltaIdelta* = Ö3VLIL*
Thus Pdelta = Ö3VLIL cos f, Qdelta = Ö3VLIL sin f
For a three phase system
Apparent Power S = Ö3VLIL
Active Power P = Ö3VLIL cos f
Reactive Power Q = Ö3VLIL sin f

## Slide 13: Analysis of three phase balanced systems
Sufficient to calculate for just one phase (usually phase A)
Figure 5 – Three phase system
EA
EB
EC
zs
zs
zs
zline
zline
zline
ZL
ZL
ZL
N
S

## Slide 14: (a) Single circuit of a three phase system
For a balanced 3 phase 3 wire system (with neutral wire absent).
supply voltages EA, EB and EC, 1200 out of phase.
potential of star point S of load is equal to potential of neutral N of supply.
whether a neutral wire is present or not, the analysis of the system becomes identical.
Ep
zs
zline
Vp
Ip
Figure 6 – One phase of Three phase system
Pp

## Slide 15
Draw neutral wire of zero impedance between S and N.
as no potential difference exists between S and N, analyse only one single phase “A” of system as shown in figure 6.
Comparing the line quantities,
EL = Ö3 Ep, IL = Ip and Pp = P/3
Usually, knowing voltage and power are more important from practical considerations, than current.
Thus reformulate problem to give voltage and power at the desired values, at the expense of a wrong current.
Multiply source voltage Ep in figure 6 by Ö3.
increases both current Ip and voltage Vp by Ö3.
Phase voltages become line voltages (Ö3 times)
Phase power becomes total power (Ö3Ö3 or 3 times)
Line current increases to Ö3 times higher (error).

## Slide 16: (b) Equivalent circuit for 3 phase balanced system
EL=Ö3 Ep
zs
zline
ZL
VL =Ö3 Vp
Ö3IL=Ö3 Ip
Figure 7 – Equivalent single phase of Three phase system
P = 3Pp
Known as equivalent single phase diagram and gives
Correct voltage as for 3 phase system
Correct power as for 3 phase system
but with current being in error by Ö3 times.

## Slide 17: Example
A three phase 400V, 50 Hz, balanced supply feeds a balanced load consisting of (a) three equal single phase loads of (40 + j 30) W connected in star, and (b) a three phase heating load (purely resistive) of 1.8 kW.
Determine the supply current, supply power factor, active and reactive power supplied and value of capacitances that must be connected in delta to improve overall power factor to 0.95 lag.
Obtain the result using
one phase of the three phase system, and
the equivalent single phase circuit.

## Slide 18: Solution
Ep
ZL2
Vp
Ip
Figure 8 – Single phase diagram
ZL1
Ip1
Ip2
(i) Using one-phase diagram
ZL1 = 40 + j 30 W
Ep = 400/Ö3 = 230.90
Pp = 1.8/3 = 0.6 kW = 600 W

[Note: Quite often, phase voltage of 3 phase 400V system is taken as 230V rather than calculated value of 230.9 V, which gives a slightly different answer.]

## Slide 19
Using P = V I cos f.

[Note: angle is zero because it is purely resistive]
Thus Ip = Ip1 + Ip2 = 4.619-36.870 + 2.598
= 6.293 – j 2.771 = 6.876-23.770 A
 supply current = 6.876-23.770 A
supply power factor = cos (0 – (-23.770)) = 0.915 lag
active power supplied = Ö3VLIL cos f = Ö34006.8760.915
= 4360 W
reactive power supplied = Ö3VLIL sin f
= Ö3  400  6.876  sin (-23.77) = 1920 var
Capacitances are connected to improve power factor to 0.95.

## Slide 20
P
Q
Qnew
Qcap
Figure 9 – Power factor correction
With pure capacitance, active power remains at P = 4.360 kW.
Qcapacitance = Qoriginal – Qnew
Qcap = 1.920 – 1.433 = 0.487 kvar
Each of 3 capacitors would provide 1/3 of this reactive power.
 Q per capacitance = 0.487/3 = 0.162 kvar = V2 C w
If capacitors are connected in delta, then line voltage would appear across each.

## Slide 21
162 = 4002 C 100 p
C = 3.230 mF each connected in delta
If capacitors are connected in star, then phase voltage would appear across each.
162 = 230.92 C 100 p
C = 9.689 mF each connected in star
Usual to connect capacitors in delta as the value required would be smaller.

## Slide 22: (ii) Using equivalent single-phase diagram
I1
Figure 9 – Equivalent diagram
EL
ZL2
VL
I = Ö3IL
ZL1
I2
ZL1 = 40 + j 30 W
EL = 4000
P = 1.8 kW = 1800 W
using P = Ö3 VL IL2 cos f = VL I2 cos f.

Ö3IL = I = I1 + I2 = 8-36.870 + 4.5 = 10.9 – j 4.8 = 11.910-23.770 A
 supply current=11.910-23.770 /Ö3 = 6.876-23.770 A (same)
[angle is zero because it is purely resistive]

## Slide 23: Unbalanced three phase systems
(a) Star connected supply feeding a star connected load
Figure 10 – Unbalanced Three phase system
ER
EY
EB
zs
zs
zs
zline
zline
zline
ZLR
ZLY
ZLB
N
S
Zneutral

## Slide 24
ILR =
, ILY =
, ILB =
Then load voltages etc can be determined.
(ii) If Zneutral  0
using Millmann’s theorem, determine voltage of the star point
(i) If Zneutral = 0

## Slide 25
Load currents can be determined from
, ILY =
, ILB =
Hence the remaining quantities can be determined.
(iii) If 3-wire system, rather than 4-wire system, analysis would correspond to zneutral =  (1/zneutral = 0).
Millmann’s theorem is used to determine VSN and the load currents are then determined.
ILR =

## Slide 26: (b) Delta connected supply feeding a star connected load
not common in practice
write Kirchoff’s current law equations for the loops and solve as a normal circuit problem.
zline
zline
zline
ZLR
ZLY
ZLB
Figure 11 – Delta supply feeding star load
S
EBR
ERY
EYB
zs
zs
zs

## Slide 27: (c) Delta connected supply feeding a delta connected load
Figure 12 - Delta connected supply feeding a delta connected load
zline
zline
zline
EBR
ERY
EYB
zs
zs
zs
Line voltages are known so that currents inside delta can be obtained directly from Ohm’s Law.
Line currents can then be obtained by phasor addition of currents inside the delta. The remaining variables are then obtained directly.

## Slide 28: (d) Star connected supply feeding a delta connected load
Figure 13 - Star connected supply feeding a delta connected load
zline
zline
zline
ER
EY
EB
zs
zs
zs
From phase voltages the line voltages are known. Currents inside the delta can be obtained directly from Ohm’s Law. Remaining variables are then obtained.

## Slide 29: Symmetrical Components (or Sequence Components)
Phase Sequence
Phase sequence is the sequence (or order) in which the three phases (voltages or currents) reach a particular position (for example peak value or zero).
t
Notes: The next section we are going to learn is symmetrical components. Before I start on that let me ask you a simple question. If you had 2 forces to add you would probably use the parallelogram law or the triangular law to do the addition. However, if you had many 3 dimentional forces to add, you would probably resolve them into 3 perpendicular directions, and do the addition axis-wise and then combine. The three axis on which you resolve need to be perpendicular to each other as each of the components should not have a component in the other direction.
The same is true with unbalanced three-phase voltages and currents. We need to resolve them into symmetrical components, or sequence components.
To do that we need to first understand Phase sequence. Phase sequence is the sequence, or order, in which the three phases, namely voltages or currents, reach a particular position, for example peak value or zero. In the balanced 3 phase waveforms shown, if we start with “A”, then if we consider the peak values, the peak of “B” occurs after that of “A” and the peak of “C” occurs after that of “B”. The peak of “A” again occurs after that. Thus the phase sequence is said to be “A-B-C”, or “A-B-C-A-B-C-A” etc. The phase sequence A-B-C is the same as the phase sequence B-C-A is the same as the phase sequence C-A-B. It is occurring cyclically. However, the phase sequence A-C-B or C-B-A or B-A-C are opposite to that of A-B-C. Instead of looking at the positive peak values, we could have looked at the negative peak values, or even the up-going zeros, or even the down-going zeros, all of which would have given the same result.

## Slide 30: Decomposition of unbalanced three-phase
In this example, sequence is A-B-C.
In 1918 Fortescue formulated that any unbalanced system can be split up into a series of balanced systems. The normal balanced system of voltages (or currents) will only have the natural sequence, and no other components present.
Notes: Let us now consider the decomposition of unbalanced three-phase phasor A-B-C shown on the left, with phase sequence A-B-C into three balanced sets of phasors as formulated by Fortescue in 1918.
The normal balanced system of voltages (or currents) will only have the natural sequence, and no other components present, like a line in the x-direction cannot have y or z components.
The three sets of balanced components defined in sequence components are: first, a balanced three phase system A1-B1-C1 having the same phase sequence as the original A-B-C and called the positive sequence; second, a balanced three phase system A2-C2-B2 having the opposite phase sequence to the original A-B-C and called negative sequence; and third, a set of 3 equal phasors A0-B0-C0 moving together and having no sequence, and called zero sequence.

## Slide 31
Unbalanced three phase system, can be split up into
a balanced system having same phase sequence as the unbalanced system, [Positive Sequence]
a balanced system having the opposite phase sequence to the unbalanced system (rotation of phasors is always anticlockwise whether they are in same sequence or opposite), [Negative Sequence] and
a balanced system of inphase quantities [Zero Sequence].
Notes: That is, an Unbalanced three phase system, can be split up into
a balanced system having same phase sequence as the unbalanced system, [Positive Sequence]
a balanced system having the opposite phase sequence to the unbalanced system (rotation of phasors is always anticlockwise whether they are in same sequence or opposite), [Negative Sequence] and
a balanced system of inphase quantities [Zero Sequence].

## Slide 32
In any 3-phase system, phase quantities A, B and C is expressed as phasor sum of
a set of balanced positive phase sequence quantities A1, B1 and C1 (phase sequence a-b-c : same sequence as original unbalanced phasors),
a set of balanced negative phase sequence currents A2, B2 and C2 (phase sequence a-c-b: opposite sequence to unbalanced phasors),
a set of identical zero phase sequence values A0, B0 and C0 (in-phase, no phase sequence).
Figure 15 - Regrouping
A1
A2
A0
A
Notes: To understand how these sequence components may be determined, let us first look at it from the other way round. The addition of the components of any particular phase, for example A0, A1 and A2 will give A, similarly B0, B1 and B2 will give B, and Co, C1 and C2 will give C as shown.

## Slide 33
Original unbalanced system has
3 complex unknown quantities A, B and C
magnitude and phase angle of each is independent.
Balanced components has
only one independent complex unknown each.
effectively 3 complex unknown quantities.
usually selected as components of the first phase A (i.e. A0, A1 and A2) .
A = A0 + A1 + A2
B = B0 + B1 + B2
C = C0 + C1 + C2
C
Notes: Now let us compare the original system and the balanced components.
The Original unbalanced system has 3 complex unknown quantities A, B and C, with magnitude and phase angle of each being independent, or 3 independent complex quantities.
The balanced components on the other hand have only one independent complex unknown each, again effectively 3 complex unknown quantities.
It is usual to select these independent quantities as the components of the first phase A (i.e. A0, A1 and A2) .
As is obvious, each phase component is made up of its own three components. Thus A = A0+A1+A2 , B = B0+B1+B2 , and C = C0+C1+C2

## Slide 34
Most frequently occurring angle is 1200.
In complex number theory, define j as anti-clockwise by 900
i.e. j = 1 900 = -1
Define a new complex operator a which
has a magnitude of unity
rotates any complex number anti-clockwise by 1200.
i.e. a = 1 1200 = – 0.500 + j 0.866
Let us again examine the sequence components of the unbalanced quantity and express B phase and C phase in terms of A phase and operator a.
. j = 1 900
a = 1 1200
Notes: The most frequently occurring angle in the symmetrical components is 1200.
In complex number theory, we define j as anti-clockwise by 900 so that j equals 1 900 or -1
Likewise, for Symmetrical component analysis we define a new complex operator  which has a magnitude of unity and rotates any complex number anti-clockwise by 1200. Thus  equals 1 1200 or – 0.500 + j 0.866
Let us again examine the sequence components of the unbalanced quantity by expressing B phase and C phase in terms of A phase and operator .

## Slide 35
Figure 16 – Decomposition of unbalanced three phase
Express all sequence components in terms of the quantities for A phase using properties of rotation of 00, 1200 or 2400.
A = A0 + A1 + A2
B = A0 + a2 A1 + a A2
C = A0 + a A1 + a2 A2
Notes: Let us now express all sequence components in terms of the symmetrical components for A phase using properties of rotation of 00, 1200 or 2400, as 1, alpha and alpha squared. Thus A = A0 + A1+ A2, B = A0 + 2 A1 +  A2, and C = A0+  A1 + 2 A2

## Slide 36
This can be written in matrix form.
Ph – phase component vector
Sy – symmetrical component vector
[L] – symmetrical component matrix.
Since the matrix is a [33] matrix, it is possible to invert it and express Sy in terms of Ph.
Let us now look at some properties of a.
Notes: This relationship between phase components A,B,C and symmetrical components A0, A1, A2 can be written in matrix form as shown with “Ph” being the phase component vector, “Sy” being the symmetrical component vector, and matrix lamda being the symmetrical component matrix.
Since the matrix is a 3 by 3 matrix, it is possible to invert it and express Sy in terms of Ph.
Let us now look at some properties of .

## Slide 37: Some Properties of a
a = 12p/3 or 11200
a2 = 14p/3 or 12400 or 1-1200
a3 = 12p or 13600 or 1
a3 - 1 = ( a - 1)( a2 + a + 1) = 0
Since a is complex, a  1,
a - 1 cannot be zero.
 a2 + a + 1 = 0
Also has the physical meaning that the three sides of an equilateral triangles must close.
Also a-1 = a2 and a- 2 = a
Notes: Now we know that  = 12/3 or 11200 so that 2 = 14/3 or 12400 or 1-1200, 3 = 12 or 13600 or 1.
Since alpha cube equals one, 3 – 1 = 0, which may be factorized as ( - 1)(2 +  + 1) = 0
Since  is complex and not equal to 1,  - 1 cannot be zero. Therefore 2 +  + 1 = 0
This statement also has the physical meaning that the three sides of an equilateral triangles must close.
Also some more important properties of alpha are alpha inverse equals alpha squared and alpha to the minus 2 equals alpha.

## Slide 38: Inverse of Symmetrical component matrix
, so that
Notes: Let us now see how the inverse of the symmetrical component matrix lambda could be obtained.
As is normal, the inverse of the matrix is obtained by taking the transpose of the co-factor determinant and dividing it by the discriminant.

## Slide 39
[L]-1 =
and discriminant D = 3(a - a2) = 3a (1-a)
Since a-1 = a2, a- 2 = a and 1 + a + a2 = 0,
[L]-1 =
Notes: When obtaining the inverse, it is seen that the matrix thus obtained can be factorized, with 1 minus alpha being a common factor.
The discriminant of the matrix can be obtained as 3 times alpha minus alpha squared which again has the factor one minus alpha.
Eliminating this common factor 1 minus alpha which appears both in the numerator in all terms and in the denominator of the discriminant gives the matrix shown. Using the properties derived from 1 plus alpha plus alpha squared equals zero, the matrix can be further simplified.

## Slide 40
a is the complex conjugate of a2,
a2 is the complex conjugate of a.
Matrix [D]-1 is one-third of complex conjugate of [D].
i.e. [L]-1 =
[L]-1 =
[L]*
Notes: Finally, the inverse of the matrix lambda is obtained as shown.
It is to be noted that  is the complex conjugate of  squared, and  squared is the complex conjugate of .
Finally, it is seen that the matrix lambda inverse is one-third of complex conjugate of the matrix lambda.

## Slide 41
This can now be written in the expanded form as
Notes: Thus the symmetric component vector A0, A1, A2 can now be written in the expanded form as one-third the matrix lambda conjugate multiplied by the phase component vector.

## Slide 42: Example1
Find the symmetrical components of unbalanced system of voltages
100 V, 3-1200 V and 2900 V.
Solution
Writing the matrix equation
Expansion of this is shown in the next slide.
Notes: Let us now consider an example to see how the sequence components can be determined. In this example, I have defined the phase components as VR, VY and VB according to an earlier system. However, the analysis is the same if they are labelled VA, VB and VC.
From the diagram it is seen that VR is 1 angle 0degree volt, VY is root 3 angle minus 120 degree volt, and VB is 2 angle 90 degree volt.
These values are put to the matrix equation is shown.

## Slide 43
VR0 =
[100 +3-1200 + 2900]
[1 - 3/2 – j3/2 + j2] =
= 0.045 + j 0.167 = 0.17375.00 V
VR1 =
[100 +112003-1200 +124002900]
[1 + 3 +3 – j1]
[4.464 – j1] = 1.488 – j0.333 = 1.525-12.60 V
VR2 =
[100 +124003-1200 + 112002900]
[1 - 3/2 + j3/2 -3 – j1]
[-1.598+j0.5]= -0.533+j0.167= 0.558162.60 V
=
[0.134 + j 0.5]
=
=
=
=
Notes: Expansion of the symmetrical component matrix equation is shown.
These give the values of the sequence components of phase R as VR0 equals 0.173 angle 75.0 degree volt, 1.525 angle minus 12.6 degree volt, and 0.558 angle 162.6 degree volt.
It is pertinent to note that VR1 has the largest magnitude of the 3 components, as is usual.

## Slide 44: Graphical Method of Solution
Figure 19 Unbalanced Phasors
VC= 2V
VA= 1V
VB= 3V
60o
A graphical solution gives an insight to components very quickly without need of a rigorous analysis.
Multiplication by a or a2 would correspond to an anticlockwise rotation of 1200 or 2400 respectively.
Example 2
For the unbalanced set of phasors shown, verify graphically the sequence components obtained in example 1.
Notes: Symmetrical component analysis can not only be done using complex numbers, but can also be done in the graphical form by sketching the phasor addition as will be shown. The same example is considered.

## Slide 45: Solution
VA0 =
or 3VA0 =
More common to determine 3VA0 rather than VA0 and to obtain one-third the result.
Visual inspection gives resultant to have a magnitude of about half of VA (say 0.5) and an angle of slightly greater than that of the VB (say 750). This corresponds to 3 VA0.
VC= 2V
VA= 1V
VB= 3V
3VA0
Compare result with that of the analytical method where the value for 3 VA0 should be 30.17375.00 V agreeing with the observation.
Notes: First let us determine the zero sequence component VA0 (or VR0 in the earlier problem). In fact, it is easier to determine 3 VA0 rather than VA0 and is a common practice to simply calculations.
As 3VA0 equals the addition of VA, VB and VC, graphical addition of the corresponding phasors gives the result 3 VA0.
Compare result with that of the analytical method where the value for 3 VA0 should be 30.17375.00 V agreeing with the observation.

## Slide 46
Similarly, VA1 =
Figure 21
1200
2400
or 3VA1 =
It is seen that resultant has a magnitude of slightly greater than 1½ times that of VA & VB
(say 4.2) together and an angle close to 150 below the horizontal axis. This corresponds to 3 VA1.
Compare the result with that of analytical method in example 1, where the value for 3VA1
should be 31.525-12.60 V agreeing with the observation.
Notes: Similarly the positive sequence voltage VA1 can be obtained as 3VA1 as the addition of VA, alpha times VB and alpha squared times VC.
This means that when phasor addition is done, VA is drawn, then VB is drawn and rotated anticlockwise by 120 degrees, and then VC is drawn and rotated by 240 degrees and added to give 3 times the required positive sequence value.
When this result is compared with the result with that of analytical method in example 1, taking 3VA1 equal to 31.525-12.60 V agreeing with the observation from the graphical method.

## Slide 47
Figure 22
2400
1200
VA2 =
or 3VA2=
Resultant has a magnitude of slightly less than that of VB (say 1.7) together and an angle close to 150 above the negative horizontal axis. This corresponds to 3 VA2.
If we compare the result with that of the analytical method in example 1, the value for 3VA2 should be 30.558162.60 V roughly agreeing with the observation.
Notes: 3VA2 is similarly obtained by the addition of VA, VB rotated anticlockwise by 240 degrees and Vc rotated anticlockwise by 120 degrees. Answers obtained are seen to agree with the theoretical value of the earlier example to visual accuracy.

## Slide 48: Summary
Vp = [L] Vs , Ip = [L] Is
Vs = ⅓[L]* Vp , Is = ⅓[L]* Ip
, [L]-1 =
[L]* =
Notes: Let us now summarise the finding so far.
The symmetrical component analysis is actually applied to either voltages or currents, and not as just ‘Sy” and “ph”.
Thus phase voltage vector Vp equals lambda matrix times symmetrical component voltage vector Vs, Ip equals lambda Is, Vs equals one-third lambda conjugate Vp, and Is equals one-third lambda conjugate Ip.
The Lambda matrix and the lambda inverse matrix have values as shown. It should also be noted that the lambda inverse matrix is in fact equal to one-third the conjugate of the symmetrical component lambda matrix.

## Slide 49: Sequence Impedances
How does impedance appear in sequence components ?
Vp = [Zp].Ip
Substitution gives
[L] Vs = [Zp]. [L] Is
pre-multiplying equation by [L]-1 gives
Vs = [L]-1.[Zp]. [L] Is
i.e. Vs = [Zs].Is
Notes: In any type of analysis, in addition to the voltages and currents, their ratio, namely impedance, and their product, namely power need to be evaluated.
How does impedance appear in sequence components ?
The phase voltage vector Vp is related to the phase current vector Ip by the phase impedance matrix Zp.
Substitution for Vp and Ip in terms of symmetrical component vectors Vs and Is gives lambda Vs equals Zp lambda Is
pre-multiplying equation by lambda inverse gives Vs equals lambda inverse Zp lambda times Is.
Meaningful grouping gives Vs = Zs time Is, where Zs equals lambda inverse Zp lambda

## Slide 50
Ra
La
Rb
Lb
Rc
Lc
Mab
Mbc
Mca
Figure 23 – 3 phase transmission line
Thus [Zs] = [L]-1.[Zp].[L]=
In a similar manner,
[Zp] = [L].[Zs]. [L]-1 =
[L].[Zs]. [L]*
Consider the sequence impedance matrix for practical problems such as the transmission line,
[L]*.[Zp].[L]
Notes: If we replace one-third lambda conjugate for lambda invers, we get matrix Zs equals one-third lambda conjugate times Zp times lambda.
In a similar manner, Zp can be caculated from one-third lambda times Zs times lambda conjugate
Symmetrical component impedance can be shown to take the form of a diagonal matrix for symmetrical practical problems like the transmission line.
In a transmission line, we can usually take the resistance of each phase to be the same, and to a great extent even the inductance of each phase can be taken to be the same. Also, the three mutual inductances can be considered to be the same.

## Slide 51
It can be assumed that the self impedance components are equal for each phase.
i.e. Ra = Rb = Rc and La = Lb = Lc
Also all 3 phase conductors behave similarly, so that mutual coupling between phases are also equal.
i.e. Mab = Mbc = Mca
In such a situation, impedance matrix would be fully symmetrical,
Notes: Symmetrical component impedance can be shown to take the form of a diagonal matrix for symmetrical practical problems like the transmission line.
In a transmission line, we can usually take the resistance of each phase to be the same, and to a great extent even the inductance of each phase can be taken to be the same. Also, the three mutual inductances can be considered to be the same giving rise to a symmetrical, but full impedance matrix in phase components.

## Slide 52
Then the symmetrical component impedance matrix is
Notes: For this perfectly symmetrical phase component impedance matrix with diagonal terms (self term) equal to Zs and off diagonal terms (mutual terms) Zm, the symmetrical component matrix can be calculated as shown.

## Slide 53
Using the property 1+a+a2 = 0, this simplifies to:
i.e.
Notes: Using the properties of 1 plus alpha plus alpha squared equal to zero, the symmetrical component matrix for the transmission line works out to a diagonal matrix with diagonal terms Z0, Z1 and Z2.

## Slide 54
Problem is very symmetric, but solution cannot be written without solving
Problem is very simple to solve by inspection as each equation has only one unknown variable.
While the phase component impedance matrix was a full matrix, although it had completely symmetry, the sequence component impedance matrix is diagonal.
Advantage of diagonal matrix is that it allows decoupling for easy analysis.
To understand the importance of decoupling (or a diagonal matrix), consider the following simple algebraic problems.
5 x + 3 y + 3 z = 6
3 x + 5 y + 3 z = 4
3 x + 3 y + 5 z = -10
4 x + 0 y + 0 z = 12
0 x + 5 y + 0 z = 10
0 x + 0 y + 3 z = -15
Notes: A simple set of simultaneous equations are shown to illustrate that it is much easier to solve when the matrix becomes diagonal.

## Slide 55: Power associated with Sequence Components
With phase components,
single phase
Pphase = V I cos f or Sphase = Vphase I*phase
three phase balanced system
P = 3 VL IL cos f = 3 Vp Ip cos f
Unbalanced three phase system
S =  Vphase I*phase
S = Va Ia* + Vb Ib* + Vc Ic*
Active power P is obtained as the Real part of the complex variable S.
Notes: Let us now consider the Power associated with Sequence Components
With phase components, for single phase ac, Pphase = V I cos phi or Sphase = Vphase I*phase.
And for a three phase balanced system P = 3 VL IL cos phi = 3 Vp Ip cos phi
However, for an unbalanced three phase system S = sigma Vphase I*phase giving
S = Va Ia* + Vb Ib* + Vc Ic*
Active power P is obtained as the Real part of the complex variable S.

## Slide 56
Re-written in matrix form as
which may be expanded as
S =
=
i.e. S = 3 (Va0 Ia0* + Va1 Ia1* + Va2 Ia2*)
Result is as expected, as there are 3 phases in each of sequence components taking the same power.
Thus P = 3(Va0 Ia0 cos f0 + Va1 Ia1 cos f1 + Va2 cos f2)
= 3VsT. Is*
Notes: Mathematical manipulation yields the result S = 3 (Va0 Ia0* + Va1 Ia1* + Va2 Ia2*)
Result is as expected, as there are 3 phases in each of sequence components taking the same power.
Thus P = 3(Va0 Ia0 cos phi0 + Va1 Ia1 cos phi1 + Va2 cos phi2)

## Slide 57: End of Presentation